# basis
1. Latency (RTT)
- Why: Controllers like TAC Xenta or AS-P may poll sensors or synchronize data frequently — latency impacts real-time responsiveness.
- How to Measure:
  - ping or nping between controllers (or controller ↔ test agent)
  - Within Open5GS, monitor UE ↔ PGW/UPF latency
- Goal: Compare average + jitter between 4G and 5G

2. Jitter
- Why: High jitter can break polling cycles, especially over BACnet/IP which isn't very forgiving with timeouts.
- How to Measure:
  - Use iperf3 -u -b 1M -t 60 --get-server-output
  - Wireshark capture for packet arrival intervals
- Compare: Standard deviation of delay in 4G vs 5G

3. Packet Loss Rate
- Why: Critical for protocol reliability. BACnet and Modbus can struggle under high loss.
- How:
  - iperf3 -u or ping packet count comparisons
  - BACnet object polling errors in logs
- What to Watch:
  - BACnet timeouts or retries on AS-P controller

4. Throughput
- Why: Even if building data is small, testing capacity matters when scaling.
- How:
  - iperf3 test between two nodes (e.g., test agent ↔ AS-P)
- Compare: Max throughput on 4G vs 5G

5. Session Setup Time
- Why: Time it takes to connect/reconnect matters during failovers, power cycles, or updates.
- How:
  - From Open5GS logs: UE attach → PDN connectivity time
  - From controller logs: boot → BACnet available
- Compare: Attach + bearer setup delay

6. Reconnect Time (Failover Test)
- Why: For real-time systems, failover and reconnection time is crucial.
- How:
  - Simulate modem drop/reboot
  - Measure how long AS-P or Xenta takes to resume comms

7. Round-Trip Application Response Time
- Why: Controller requests sensor data → response time
- How:
  - Use Wireshark to time BACnet ReadProperty → Ack
  - Simulate queries from test agents or actual sensors

8. CPU & Memory Usage on AS-P (optional)
- Why: See if different network conditions affect processing
- How:
  - If you can SSH or use EcoStruxure logs
  - SNMP polling, if enabled

🧪 Test Environment Summary
Scenario	Connectivity	Tool
Scenario 1	Open5GS (4G)	UE via USB dongle or modem
Scenario 2	Real 5G Network	Same test flow

If needed, you can add a PC with dual-mode modem (4G + 5G capable) acting as a traffic relay/test agent.
Helpful Tools
- Wireshark: Full BACnet/Modbus inspection
- iperf3: Bandwidth, jitter, packet loss
- PingPlotter: Visual latency trends
- YABE (Yet Another BACnet Explorer): BACnet object monitoring
- Open5GS Dashboard: Real-time monitoring of attach, bearer setup
- Prometheus + Grafana: If you want time-series metric graphs

Vragen: hoe spacelogic geconnecteerd met Xenta (LON/BACnet/enz.)
GPT: 5G diagram steken

🧩 1. Add the TAC Xenta & SpaceLogic AS-P Controller into the Setup
Since the TAC Xenta modules typically communicate via Modbus RTU (RS485) or LonWorks, and the AS-P controller can bridge that to Ethernet/IP, you'd ideally connect like this:
📶 Simplified Integration Diagram
less
KopiërenBewerken
[ TAC Xenta Modules ]
        | (RS-485 or LonWorks)
        v
[ SpaceLogic AS-P Controller ]
        | (Ethernet)
        v
[ VLAN Interface on Juniper Switch (e.g., VLAN900/901) ]
        |
   Existing 5G Network Infrastructure (PR_HOGE_x)
        |
  Remote Test Machine / Open5GS Core
You can put the AS-P on VLAN900 or VLAN901 depending on where you want to test traffic from.

📝 2. Checklist / Test Script Outline
✅ Physical + Logical Setup
- AS-P has IP address on 10.105.3.x/31 subnet (e.g., via static config or DHCP)
- TAC Xenta modules reachable from AS-P
- AS-P configured to expose data (Modbus TCP / BACnet / HTTPS API)
- VLAN900 or VLAN901 route to/from test machine confirmed
⚙️ Test Scenarios
Scenario	Description	Goal
S1	AS-P connected via 4G router (Open5GS UE simulation)	Baseline latency/jitter/throughput
S2	AS-P connected via existing 5G path (e.g., via PR_HOGE)	Measure performance delta
S3	High-traffic injection	Evaluate latency under load
S4	Fault simulation (link fail, jitter added)	Test reliability, fallback behavior

🔬 Metrics to Collect
Category	Metric	Tool / Method
Network	Latency	ping, iperf, fping
	Jitter	iperf -u, owping
	Packet Loss	iperf, ping stats
	Bandwidth	iperf3, speedtest-cli
Application	Modbus/BACnet read time	Python w/ pymodbus, bacpypes
	Read error rate	Count failures/timeouts
System	CPU / Mem usage on AS-P	SNMP / Web API / local check
	Connection drop detection	Log monitor / packet loss

🌐 Picking a 5G Gateway for S1 (Simulation)
If you're simulating 4G/5G with Open5GS on a test laptop and want a real-world baseline, here are your best picks:
🔸 Industrial Gateway
Model	Notes
Teltonika RUTX50	Great value, full 5G SA/NSA, VPN, Modbus pass-through, remote web UI
Sierra Wireless XR80	Higher-end, edge compute support, robust security
Cradlepoint IBR1700 w/ 5G adapter	Enterprise grade, NetCloud support, pricey but stable

Make sure it supports:
- Bridge mode (to pass traffic through to AS-P)
- CLI or API for stats/logs
- VLAN tagging (if you want to keep it isolated)

# Update met info 5g netwerk
🧠 Updated Understanding of 5G Setup in Building C
🔹 Prefixes
Type	Range
Customer	10.105.0.0/16
WAN	10.105.0.0/25
OAM	10.105.1.0/24
CM MGMT	10.105.2.0/24
RAN	10.105.3.0/24 ← Relevant for eNBs, gNBs, UE tests
OOB	10.105.0.128/25

🔹 Available UE Test Subnets (via APNs)
These look like PDN pools (i.e., IPs your UEs get from 5G Core):
APN / DNN	Subnet Assigned	Use this for...
apn1hogent	10.105.16.0/20	Broad range, could simulate many UEs
apn3hogent	10.105.33.0/24	Isolated slice/subnet for lab tests
apn7hogent	10.105.37.0/24	Ideal for isolated 5G test scenario (Option)

✅ What’s Next
📌 1. Connect AS-P to 5G Network
You'll need:
- AS-P in VLAN900/901, or
- Connect to the 5G Core via Open5GS UE simulation or real UE device using e.g., apn7hogent
You could test in two ways:
A) Direct 5G Core UE Emulation
Use Open5GS UE → Connect to apn7hogent → Talk to AS-P over 10.105.3.x subnet.
B) Physical AS-P + 5G Gateway
Physically connect the AS-P to a Teltonika RUTX50 (for example), and assign it to APN7.
Sample Python Script: Modbus + Network Metrics Collection
This script assumes:
- You're polling TAC Xenta modules via Modbus TCP (commonly port 502).
- You're measuring latency, packet loss, and basic throughput.
✅ Requirements:
bash
KopiërenBewerken
pip install pymodbus ping3 psutil
📜 test_modbus_network_metrics.py
python
KopiërenBewerken
from pymodbus.client import ModbusTcpClient
import ping3
import time
import psutil
import logging

MODBUS_IP = "10.105.3.10" # IP of Xenta module
MODBUS_PORT = 502
PING_TARGET = "10.105.3.10"
LOOP_DELAY = 5

def read_modbus_data(client):
    try:
        result = client.read_holding_registers(0, 2)
        if result.isError():
        return "Error"
        return result.registers
    except Exception as e:
        return f"Modbus error: {e}"

def get_latency(ip):
    try:
        latency = ping3.ping(ip, timeout=2)
        return latency * 1000 if latency else None
    except Exception:
        return None

def log_network_usage():
    stats = psutil.net_io_counters()
    return stats.bytes_sent, stats.bytes_recv

# Setup
logging.basicConfig(filename='test_metrics.log', level=logging.INFO)
client = ModbusTcpClient(MODBUS_IP, port=MODBUS_PORT)

while True:
    client.connect()

    modbus_data = read_modbus_data(client)
    latency = get_latency(PING_TARGET)
    tx, rx = log_network_usage()

    logging.info(f"[{time.ctime()}] Modbus: {modbus_data}, Latency: {latency:.2f}ms, Sent: {tx}, Received: {rx}")

    print(f"Data: {modbus_data} | Latency: {latency:.2f} ms | TX: {tx} | RX: {rx}")
    client.close()
    time.sleep(LOOP_DELAY)

🧪 What This Collects
- ✅ Modbus register reads
- ✅ Network latency
- ✅ Bytes sent/received
- 📦 You can extend it with iperf3 if you want more in-depth throughput stats.

# Open5gs
🧠 How Open5GS Can Be Used (Not Just for Simulation)
Instead of using Open5GS purely for simulation, you can use it in complementary roles to enhance your testing and learning without disrupting production 4G/5G. Here are a few realistic ideas:

🔄 1. Training / Emulation Environment
Set up a parallel lab EPC using Open5GS + srsRAN/Amarisoft to:
- Practice 4G/5G registration procedures.
- Understand how UE attaches, gets an IP, and accesses LAN (via GTP).
- Learn how to trace packet flows in EPC + analyze bearer/QoS setup.
💡 Benefit: Deep visibility into signaling (NAS/NGAP) without touching production gear.

📡 2. UE-to-Cloud Latency Comparison
Attach a test UE (e.g. Quectel modem, Raspberry Pi) to:
- Private 4G on campus (HOGENT)
- Open5GS 4G/5G
- Production 5G
Then compare latency and throughput by hitting the same endpoint.
💡 Use tools like:
bash
KopiërenBewerken
ping <cloud_endpoint>
iperf3 -c <host>

🔍 3. GTP-U Packet Path Monitoring
Use Open5GS to inspect:
- GTP-U encapsulated traffic
- Tunneling impact on throughput or jitter
- Traffic shaping or QoS behavior
💡 Deploy a lightweight GTP analysis script like Wireshark + tshark or gtp5g kernel modules.

🧪 4. Replay or Emulate AS-P + Xenta Traffic
Using Open5GS with a small LTE cell, you can:
- Connect a UE (like a USB LTE stick)
- Forward traffic to a Modbus TCP relay
- Emulate polling traffic over LTE in a controlled setup
💡 This is great for testing firewalls, NAT traversal, and time-sensitive Modbus exchanges.

🔐 5. Test Private APNs + VPN Overlay
You can test APNs like:
- apn=hogent.private.iot
- With route control via Open5GS
- Tunnel traffic back to AS-P/Xenta via VPN
💡 See how long VPN handshakes take under different cellular conditions.

# Summary
Got it — thanks for clarifying! Let’s tailor the summary specifically to reflect that the tests focus on comparing 4G vs 5G for HVAC and lighting control systems, in a building automation (BAS) context.

🧪 Network Performance Tests: 4G vs 5G for Building Automation (HVAC & Lighting)
🏢 Context: Building C, HOGENT
- Building C is equipped with a private 5G SA network (Ericsson) and a private 4G network.
- The building runs HVAC and lighting systems controlled by:
  - TAC Xenta modules (legacy HVAC/lighting controllers using Modbus)
  - Spacelogic AS-P controllers (modern BMS with Modbus TCP/IP, BACnet, etc.)

🎯 Test Objective
Evaluate and compare the performance of 4G and 5G networks for reliable, real-time control of HVAC and lighting systems, with a focus on:
- Communication latency and reliability for Modbus-over-IP
- Suitability for responsive building control
- Performance under load (congestion, interference, etc.)

🧪 Test Scenarios
🔹 Scenario 1: Using Private 4G Network
- Connect test PC or gateway (UE) to the private 4G
- Run HVAC/lighting control traffic (Modbus TCP) to AS-P → Xenta
🔹 Scenario 2: Using Private 5G Network
- Connect UE to the 5G SA network in Building C
- Run the same traffic patterns
- Measure latency, reliability, and bandwidth
🔹 (Optional): Simulated/Open5GS Lab
- Use Open5GS locally for test scenarios or stress testing
- Helps analyze how protocols behave with different core network setups

🧰 Architecture Overview
[Modbus Polling Scripts / Test PC]
        |
        (USB)
        |
  [5G/4G UE or Gateway (e.g., Teltonika)]
        |
       [Private 5G / 4G Network]
        |
      [Spacelogic AS-P Controller]
        |
       [TAC Xenta Modules]

📏 Key Metrics Collected
Metric	What it tells us	Tool
Modbus response time	Delay between request and HVAC/lighting reply	pymodbus, Wireshark
Network RTT (ping)	Base network delay	ping, fping
Packet loss	Network reliability	iperf3, ping
Jitter	Suitability for time-sensitive control	iperf3, tshark
Signal quality (RSRP/SINR)	UE connectivity quality on both networks	mmcli, uqmi
Bandwidth (up/down)	Throughput under idle and active load	iperf3, speedtest

🧪 Test Automation Tools
- Python:
  - pymodbus for Modbus TCP polling
  - pingparsing, psutil for metrics
- Bash:
  - ping, iperf3, tshark for stats
- Optionally log into InfluxDB + Grafana

🎯 Why This Test Matters
- HVAC and lighting systems are sensitive to latency and reliability.
- 5G promises lower latency and higher reliability than 4G.
- This test evaluates if 5G’s promises translate into real performance benefits for building automation use cases, particularly:
  - Real-time temperature or lighting adjustment
  - Load shedding or fault detection
  - Remote diagnostics

✅ Deliverables You’ve Built
- ✔️ Metric tracking spreadsheet (CSV/Excel)
- ✔️ Testbed architecture diagrams (.drawio/.png)
- ✔️ Python + Bash test scripts
- ✔️ Connection plan: Arduino/radio → USB → PC → 4G/5G → AS-P → Xenta
- ✔️ Optional Open5GS for signaling analysis

Would you like this wrapped into:
- A slide deck (for a presentation)?
- A technical white paper or Word doc?
- Or just continue expanding the test cases/scripts?
Let me know how you want to move forward!
HVAC/Lighting 4G vs 5G Test Setup Guide
1. Identify and Prepare the System Components
Control Devices:
- Spacelogic AS-P: Modern building controller (Modbus TCP, BACnet, etc.)
- TAC Xenta Modules: Legacy devices (usually controlled via Modbus RTU or TCP)

Network Paths:
- 4G/5G Gateway/Router: Connects to private networks (acts as UE)
- Private 4G & 5G: Already deployed on Building C
- Test PC or Raspberry Pi: Runs test scripts

Recommended Gateways:
- Teltonika RUTX50 (5G)
- Digi EX50 or IX20
- Sierra AirLink XR90
2. Physical Network Setup
[Test PC or Raspberry Pi]
|
USB or ETH
|
[4G/5G Router/UE] -- wireless --> [Private 4G or 5G network]
|
LAN port or bridge mode
|
[Spacelogic AS-P] -- Modbus --> [TAC Xenta Devices]
3. Network Configuration
On Router:
- Enable bridge mode or port forwarding
- Expose AS-P to same subnet
- Collect signal stats (SINR, RSRP, RSRQ)

On AS-P:
- Assign static IP or configure DHCP
- Enable Modbus TCP
- Map Modbus registers to Xenta devices
4. Software Setup on Test PC
Install Tools:
- sudo apt install iperf3 tshark ping jq python3-pip
- pip3 install pymodbus pingparsing psutil

Python Modbus Sample:
from pymodbus.client import ModbusTcpClient

client = ModbusTcpClient('192.168.1.10', port=502)
client.connect()
rr = client.read_holding_registers(0, 2, unit=1)
print(rr.registers)
client.close()

Bash:
ping -c 100 192.168.1.10 > ping_results.txt
mmcli -m 0 | grep -i signal
iperf3 -c 192.168.1.10
5. Metrics to Capture
- Latency: ping
- Packet Loss: ping or iperf3
- Jitter: iperf3 -u
- Modbus Response Time: measure with Python timing
- Bandwidth: iperf3
- Signal Stats: mmcli, uqmi
6. Run the Tests
1. Connect AS-P and Xenta and validate
2. Connect PC via 4G router and run tests
3. Connect via 5G router and repeat
4. Store metrics in CSV or database
7. Logging and Dashboard (Optional)
Use Telegraf + InfluxDB + Grafana to store and visualize:
- Modbus timings
- RTT
- Signal strength
8. Analysis
- Compare response times, packet loss, bandwidth
- See which network is better for control traffic
- Assess reliability of each under different conditions
Conclusion
This setup helps determine whether 5G provides tangible benefits for building automation systems like HVAC and lighting. You can decide whether to stick with 4G or upgrade based on real-world data.